## 66kV Refurbishment options - Index of OHL4, CE/C/37 and CE/C/36 structures

| Pole Assembly Drawing | Detailed Xarm Drawing | Pole Fabrication Drawing | Material List | Insulators | Description |
| --- | --- | --- | --- | --- | --- |
| Notes: Structure drawing numbers highlighted in green are available as replacements options for existing structures Structures marked (Obs) or obsolete are included for information only to show the existing structure and what it shall be replaced with |  |  |  |  |  |
| OHL4 (Single Pole Design) |  |  |  |  |  |
| Eng Inst O.311 | Existing Specification for OHL4 – Included for reference only and as a source for the historical capabilities of the old structures eg required pole grade / angles of deviation Notes: MWT of design 17.79kN utilising 70kN fittings Typical max span for 100mm AAAC – 168m on 16m stout grade poles or 200m on E/Stout (see foundations & clashing limits) Typical max span for 175mm ACSR – 100m on 16m stout grade poles or 130 on E/Stout (see foundations & clashing limits) |  |  |  |  |
| 1091231190 sht 3 | 0652 sht 1 & 3 | 1186 sht1 | 1190 3mat | NSP004127 | Single Pole, Intermediate Structure |
| 1091231191 sht 1 | 0652 sht 1 & 3 |  | 1191 1mat | NSP004127 | Single Pole, Straight Line Section Structure |
| 1091231192 sht 1 | 0652 sht 1 & 3 |  | 1192 1mat | NSP004127 | Single Pole , Section Angle, small angle structure 100mm AAAC - 25º (Stout) or 45º (E/Stout) 175mm ACSR - 5º (Stout) or 20º (E/Stout) |
| 1091231193 sht 1 (Obs) Replace with 1091390014 sht1 or 1091390018 sht1 | n/a 0675 sht6 0675 sht 50 | 434002 1390003 sht2 0018sht 2 | 1193 1mat 0014 1 mat 0018 1mat | NSP004127 | Obsolete - 1.83m Ctrs H Pole, Section Angle (Large Angle) Structure. Replace with Single E/Stout Pole , Section Angle structure, 20º – 40º or 2.9m Ctrs H Pole, Large Section Angle 40º – 60º |
| 1091231172 sht3 (obs) or 1091231173 sht 1 (obs) Replace with 1091390019 sht1 or 1091231173 sht 4 or 1091231173 sht 9 | 0308 series 1173 sht 3 & 0650 sh1 0675 sht 50 or 0675 sht 50 or 0675 sht 50 | n/a 1187 sht1 0019 sht 2 or 1173 sht 5 or 1173 sh10 | n/a 1173 1mat 0019 1mat 1173 4mat 1173 9mat | NSP004127 | Obsolete – 2.4m ctrs H Terminal (No Cable) or Obsolete - 2.9m Ctrs H Terminal Structure (No Cable) Replace with 2.9m Ctrs H Terminal Structure (No Cable) or 2.9m Ctrs H Terminal Structure (Single Core Self Supporting Cable Termination) or 2.9m Ctrs H Terminal Structure (Single Core Cable - Heat Shrink Termination |
| 1091231173 sht 2 (Obs) Replace with 1091390021 sht 1 | 1173 sht 3 & 0650 sh1 0675 sht 50 | 1187 sht1 0018sht 2 | 1173 2mat 0021 1mat | NSP004127 | Obsolete - 2.9m Ctrs H Pole, Out of Balance – Straight Line Section Assembly (Extra ordinary long Spans) Replace with 2.9m Ctrs H Pole, Out of Balance – Straight Line Section Assembly (Extra ordinary long Spans) |
| 1091231173 sht 13 | 0675 sht 50 | 1173 sht14 | 1173 13mat | NSP004127 | 2.9m Ctrs H Pole, Straight Line Section with In Line Cable Tee |
| 1091231160 sht1 | 1160 sht3 | Info Only – ‘A’ pole refurbishment – details of suspension insulator attachment plate |  |  |  |
| 1091231190 sht 4 | 0652 sht 1 & 4 | Existing ‘A’ Pole | 1190 4mat | NSP004127 | ‘A’ Pole, Intermediate refurbishment assembly |
| 1091231191 sht 2 | 0652 sht 1 & 4 |  | 1191 2mat | NSP004127 | ‘A’ Pole, Straight Line Section refurbishment assembly |
| 1091231192 sht 2 | 0652 sht 1 & 4 |  | 1192 2mat | NSP004127 | ‘A’ Pole, Section Angle, small angle refurbishment assembly |
| Drawing 1091232000 sht 1 summarises visually the historical arrangements utilised in NEDL |  |  |  |  |  |

| OHL4 (Long Span - Portal) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| MWT of design 17.79kN utilising 70kN fittings Notes: Typical max span for 100mm AAAC – 200+m on 16m stout grade H poles (see foundations & clashing limits) Typical max span for 175mm ACSR – 170m on 16m stout grade H poles (see foundations & clashing limits) |  |  |  |  |  |
| Pole Assembly Drawing | Detailed Xarm Drawing | Pole Fabrication Drawing | Material List | Insulators | Description |  |
| 1091231165 sht1 (Obs) Replace with 1091231165 sht4 | 1165 sht5 & 0675 sht 50 | 1187 sht 1 | 1165mat | NSP004127 | Obsolete - 2.9m Ctrs H Intermediate Suspension Structure Replace with 2.9m Ctrs H Intermediate Suspension Structure |  |
| Historical Intermediate portal crossarms 66.5/10.1161 sht3 | 1091010706 – Suspension Insulator attachment plate – to be replaced when insulator strings are being replaced on historical assemblies |  |  |  |  |  |
| 1091231162 sht 1 (Obs) or 1091231162 sht 2 (Obs) Replace with 1091390014 sht1 or 1091390018 sht1 | 1162 sht 3 & 0650 sh1 0675 sht6 0675 sht 50 | 1187 sht1 or n/a 1390003 sht2 0018sht 2 | 1162 2mat n/a 0014 1 mat 0018 1mat | NSP004127 | Obsolete - 2.9m Ctrs H Poles, Large Section Angle or Obsolete - Application of standard crossarm to existing pole dressed to 66.5/10.1162 Replace with Single E/Stout Pole , Section Angle structure, 20º – 40º or 2.9m Ctrs H Pole, Large Section Angle Pole 40º – 60º |  |
| 1091231163 sht 1 (Obs) or 1091231163 sht2 (Obs) replace with 1091390013 sht1 or 1091390020 sht 1 | 1163 sht 3 & 0650 sh1 0675 sht6 0675 sht 50 | 1187 sht1 n/a 1390003 sht2 0018sht 2 | 1163 2mat 1163 2mat 0013 1mat 0020 1mat | NSP004127 | Obsolete - 2.9m Ctrs H Pole , Straight Line Section Structure or Application of standard crossarm to existing 2.74m or 2.44m Ctrs H Poles dressed to 1091231163 replace with Single E/Stout Pole , Straight Line Section Pole (any cond) or 2.9m Ctrs H Pole, Straight Line Section Pole |  |
| For available terminal, cable terminal and out of balance line section structures in portal lines see 1091390019 sht1, 1091231173 sht 4, 1091231173 sht9, 1091231173 sht13 and 1091390019sht 4 |  |  |  |  |  |  |
| 1091231164 sht 1 | 1164 sht 3 | n/a | 1164 1mat | NSP004127 | Large Section Angle Structure, Application of standard crossarm to existing 2.44m Ctrs H Poles dressed to 33.41/1.640 or 66.5/10.1164 |  |

| CE/C/37 Specification |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| DSS/004/040 | Existing Specification for CE/C/37 Specification – Included for reference only and as a source for the historical arrangement drawings Notes: MWT of design 25kN utilising 125kN fittings Typical max span for 175mm ACSR – 150m on 16m stout grade H poles |  |  |  |  |  |
| CE/C/37 (M1) | Existing Specification for CE/C/37 (M1) Upgraded Specification – to cater for 200mm AAAC. Included for reference only and as a source for the historical arrangement drawings Notes: MWT of design 23kN utilising 125kN fittings Typical max span for 200mm AAAC – 150m on 16m stout grade H poles |  |  |  |  |  |
| Pole Assembly Drawing | Detailed Xarm Drawing | Pole Fabrication Drawing | Material List | Insulators | Description |  |
| Y104L0101 (obs) or Y104L0112 (obs) Replace with 1091231165 Sht 4 | 1165 sht 5 & 0675 sht 50 | Existing Pole fabrication drawings 1187 sht1 | 1165mat | Original tension fittings NSP004127 | Obsolete – 2.44mm Ctrs H Portal H Intermediate Suspension Structure Replace with 2.9m Ctrs H Portal H Intermediate Suspension Structure |  |
| Y104L0102 (obs) or Y104L0113 (obs) Replace with 1091390013 sht1 or 1091390020 sht 1 | 0675 sht6 0675 sht 50 | Existing Pole fabrication drawings 1390003 sht2 0018sht 2 | 0013 1mat 0020 1mat | Original tension fittings NSP004127 | Obsolete – 2.44m Ctrs H Pole Straight Line Section – see DSS/004/040 for details Replace with Single E/Stout Pole , Straight Line Section Pole or 2.9m Ctrs H Pole, Straight Line Section Pole |  |
| Y104L0103 (obs) or Y104L0114 (obs) Replace with 1091390013 sht1 or 1091390018 sht1 | 0675 sht6 0675 sht 50 | Existing Pole fabrication drawings 1390003 sht2 0018sht 2 | 0013 1mat 0018 1mat | Original tension fittings NSP004127 | Obsolete – 2.44m Ctrs H Pole Angle Section 0-10º – see DSS/004/040 for details Replace with Single E/Stout Pole , Section Angle structure, 0º – 20º or 2.9m Ctrs H Pole, Large Section Angle Pole 40º – 60º |  |
| Y104L0104 (obs) or Y104L0115 (obs) Replace with 1091390014 sht1 or 1091390018 sht1 | 0675 sht6 0675 sht 50 | Existing Pole fabrication drawings 1390003 sht2 0018sht 2 | 0014 1 mat 0018 1mat | Original tension fittings NSP004127 | Obsolete – 2.44m Ctrs H Pole Angle Section 10-60º – see DSS/004/040 for details Replace with Single E/Stout Pole , Section Angle structure, 20º – 40º or 2.9m Ctrs H Pole, Large Section Angle Pole 40º – 60º |  |
| Y104 L0106 or |  |  |  |  |  |  |
| MWT of conductors used with this design and thus minimum ratings for tension fittings |  |  |  |  |  |  |
| Design Tensions |  |  |  |  | Min Tension Fitting Rating | New Drawing no |
| .175” / 175mm ACSR – erected pre 1999 = 26kN , Post 1999 = 25.7kN .2” / 125mm HDBC – erected pre 1974 = 25kN 200mm AAAC – Post 1998 – 23.51kN .150” / 150mm ACSR – erected pre 1974 = 22.49kN), Post 1974 = 19.68kN .15” / 100mm HDBC erected pre 1974 = 18.97kN, Post 1974 = 18.81kN .1” / 70mm HDBC – erected pre 1974 = 13kN, post 1974 = 13.43kN |  |  |  |  | Requires 125kN Tension Fittings Requires 125kN Tension Fittings Requires 125kN Tension Fittings Requires 70kN Tension Fittings Requires 70kN Tension fittings Requires 70kN tension fittings | 1091010488 sht 9 1091010488 sht 9 1091010488 sht 9 1091010488 sht 8 1091010488 sht 8 1091010488 sht 8 |

|  | CE/C/36 – 33kV Lines |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MWT of design - Various Tensions utilising 70kN or 125kN fittings Typical max span for 175mm ACSR – 76 or 91m on 16m stout grade poles |  |  |  |  |  |  |  |  |
| Pole Assembly Drawing | Detailed Xarm Drawing | Pole Fabrication Drawing | Material List | Insulators |  | Description |  |  |
| Y003 X 1102 (Obs) Replace with 1000434004 | Crossarms 439557 | Existing Pole fabrication drawings 1000434001 | 4004 mat | Original tension fittings NSP004127 |  | Obsolete - 33kV Intermediate Pole with pin or post insulators on a single pole Replace with 33kV Intermediate Pole on a single pole (43-40) |  |  |
| Y003 X 1102 (Obs) Replace with 1000434005 | Crossarms 439520 | Existing Pole fabrication drawings 1000434001 | 4005 mat | Original tension fittings NSP004127 |  | Obsolete - 33kV Straight Line Section - Rutter Pole Replace with 33kV Single Straight Line Section pole on single pole (43-40) |  |  |
| Y003 X 1102 (Obs) Replace with 1000434004 or 1000434005 | Crossarms 439557 Or 439520 | Existing Pole fabrication drawings 1000434001 Or 1000434001 | 4004 mat or 4005 mat | Original tension fittings NSP004127 |  | Obsolete - 33kV Section Angle Pole - Rutter Pole -0º – 40º Replace with 33kv Pin Angle – Single Stout Pole 6º Deviation or 33kV Section Angle Pole – Single E/Stout Pole 40º dev (175mm ACSR) or 34º dev for (125mm HDBC) |  |  |
| Y104L0104 (obs) or Y104L0115 (obs) Replace with 1091390018 sht1 | 0675 sht 50 | 0018sht 2 | 0018 1mat | Original tension fittings NSP004127 |  | Obsolete – 2.44m Ctrs H Pole Angle Section 40-60º – see DSS/004/040 for details Replace with 2.9m Ctrs H Pole, Large Section Angle Pole 40º – 60º |  |  |
| Y104 L0106 (Obs) or Y104 L0109 (Obs) Replace with 1000434011 or 1000434011 sht 6 1000434011 sht 8 | 439522 439522 439522 | 434002 sht2 434002 sht2 434002 sht2 | 4011 mat | Original tension fittings NSP004127 |  | Obsolete – 33kV H Cable Terminal Poles Replace with 33kV 1.83m Ctrs H Terminal Pole – No Cable 33kV 1.83m Ctrs H Cable Terminal Pole – Heat Shrink Cable 33kV 1.83m Ctrs H Cable Terminal Pole – Self Supporting Cable Term |  |  |
| MWT of conductors used with this design and thus minimum ratings for tension fittings |  |  |  |  |  |  |  |
| Design Tensions |  |  |  |  | Min Tension Fitting Rating |  | New Drawing no |
| .2” / 125mm HDBC – erected pre 1974 = 25kN .175” / 175mm ACSR – erected pre 1974 = 22.27kN , Post 1974 = 22.85kN .150” / 150mm ACSR – erected Post 1974 = 19.68kN .15” / 100mm HDBC erected pre 1974 = 18.97kN, Post 1974 = 18.81kN .1” / 70mm HDBC – erected pre 1974 = 13kN, post 1974 = 13.43kN |  |  |  |  | Requires 125kN Tension Fittings Requires 70kN Tension Fittings Requires 70kN Tension Fittings Requires 70kN Tension fittings Requires 70kN tension fittings |  | 1091010488 sht 9 1091010488 sht 9 1091010488 sht 8 1091010488 sht 8 1091010488 sht 8 |

| Common Insulator Assemblies used in the renovated or replacement structures |  |  |
| --- | --- | --- |
| Drawing Number | Associated material list in NSP/004/127 | Description |
| 1091010488 sht6 | 0488 6mat | 70kN Suspension Insulator Assembly for use on OHL4 or CE/C/37 Lines |
| 1091010488 sht8 | 0488 8mat | 70kN Tension Insulator Assembly for use on OHL 4 Lines |
| 1091010488 sht9 | 0488 9mat | 125kN Tension Insulator Assembly for use on CE/C/37 Lines |
| 1091010487 sht13 | n/a | 12.5kN 66kV Post/Pilot Insulator for OHL4 Lines |
| 1091010487 sht12 | n/a | 4.5KN Pilot Post Insulator with Single 50mm Mounting Stud |

| Special CE/C/37 insulator string components used when renovating string sets |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 70kN Ball-ended Eye link | 125kN Shackle | 70kN Extended Ubolt | Suspension Clamp for Aluminium Conductors | Suspension Clamp for Copper Conductors | 70kN crossarm Strap | 125kN crossarm strap |

Last update 25/08/10