## Drawing guide - CURRENT
Drawing arrangement description | Pole arrangement drawing number (Drawings used to construct pole to on site) | Pole Fabrication drawing number (Drawings used by pole fabricators) | Fab drawing variations | To be confirmed with customer before quoting | Minimum pole top diameter before fabrication | Resource Pole | 439103 type 1 | 439103 type 2 | 439103 type 3 | 439103 type 4 | 1.09.101.0675 sheet 30 item 10 | 1.01.109.0650 Sheet 3 Item 8
[7 empty] | 125 250 0850 | 125 250 1300 | 125 250 1500 | 125 250 2500 | 125 250 1300 | 125 250 3600
Single Pole | 1091231160 | 1091231160 sht5 |  |  | As per standard minimum size shown in BS1990 table
Single Pole Intermediate | 1091380006 sht1 | 1091380006 sht2 |  |  | As per standard minimum size shown in BS1990 table |  |  | 1 |  | 1
Rutter Pole Intermediate | 1091390016 sht1 | 1091390008 sht2 |  | Do the poles need the ladder holes drilling | As per standard minimum size shown in BS1990 table | [5 empty] | 4
Rutter St Line Section Pole | 1091390016 sht1
132kV Rutter Pole | 1091390017 sht1
|  | 1091390003 sht2 |  | Do the poles need the ladder holes drilling | 12.0m - 245mm | D Whiley confirmed that we would use a pole two sizes up but pick ones with big tips to suit the requirement |  | 2
*Single Pole Straight Line Section / Section Angle Pole up to 20° | 1091390013 sht1 |  |  |  | 13.0m - 245mm
*Single Pole Section Angle Pole 20° - 40° | 1091390014 sht1 |  |  |  | 14.0m - 245mm
*Single Pole Section Angle Pole 40° -60° | 1091390015 sht1 |  |  |  | 15.0m - 245mm
16.0m - 250mm
17.0m - 250mm
132kV Section / Angle H Pole |  | 1091380003 sht2 C |  |  | 250mm |  |  | 4 |  |  |  | 1
H Pole Terminal Pole – No cable termination up to 132kV | 1091390019 sht1 | 1091390019 sht2 F |  |  | 226mm |  | 4 | 4 |  |  |  | 1
H Pole Terminal Pole – Cable termination (up to 66kV only) | 1 09 123 1173 sht4 L General arrangement | 1 09 123 1173 sht5.pdf |  | Confirm fab drawing | 230mm
H Pole Terminal Pole - 66kV | 1 09 123 1173 sht9 C General arrangement | 1 09 139 0019 sht2 F.pdf |  | Confirm fab drawing | 226mm
H Pole Terminal Pole - 66kV |  | 1 09 123 1173 sht10.pdf |  | Confirm fab drawing | 230mm
H Pole Intermediate - 66kV |  | 1 09 123 1173 sht14 A.pdf |  | Confirm fab drawing | 230mm
H Pole Terminal Pole - 66kV |  | 1 09 123 1173 sht19 A.pdf |  | Confirm fab drawing | 230mm
| 1091390018 sht1 | 1091390018 sht2 |  | Do the poles need the ladder holes drilling | 226mm |  | 4 | 4 |  |  |  | 1
H Pole St Line Section Pole | 1091390020 sht1
H Pole St Line Section Pole (Out of Balance stays) | 1091390021 sht1
H Pole Intermediate (post Insulators) | 1091390022 sht1
Single Section Pole | 1091231191 sht1 | 1091231186 sht1 |  | Stout or Extra Stout | 210mm Stout
Single Pole | 1091231190 sht3 |  |  |  | 250mm Extra Stout
H Pole Portal type | 1091231165 sht4 | 1091231187 sht1 Revison O |  |  | 195mm |  |  | 2
H Portal Support CE/C/37 | Y104L0112 | Y204L0601 Type 1A | H Intermediate |  | 205mm
| Y104L0113 | Y204L0601 Type 1A | H Section |  | 215mm
| Y104L0114 | Y204L0601 Type 2 | H Angle up to 10⁰ |  | 20mm above minimum stated tip diameter in BS1990
| Y104L0115 | Y204L0601 Type 2 | H Angle 10⁰ to 60⁰ |  | 20mm above minimum stated tip diameter in BS1990
| Y104L0116 | Y204L0601 Type 3 | H Terminal |  | 20mm above minimum stated tip diameter in BS1990
33kV Cable Termination with Surge Divertors CE/C/37M | Y104L0117 | Y204L0602 | H Terminal |  | 235mm
66kV Cable Termination with Surge Divertors | Y104L0118 | Y204L0603 | H Terminal |  | 235mm
| Y104L0108 | Y204L0604
33kV Cable Termination with Surge Divertors CE/C/37 (M1) | Y104L0109 | Y204L0605 | H Terminal |  | 235mm
Average taper of poles using BS1990 table - 11mm per metre for Stouts - 9mm per metre for Mediums - 7mm per metre for Lights

## Copy of BS1990 table
TABLE OF SIZE, WEIGHT & STRENGTH FOR CREOSOTED SCOTS PINE POLES
Class | Length (m) | Min top dia (mm) | Min dia 1.5m from butt (mm) | Volume (caliper cu m) | Indicative weight (kg) | 1 Ultimate load @ 0.6m from top of pole (kN) | 2 Load per mm deflection at point of application of load (N)
LIGHT | 6 | 125 | 150 | 0.1099 | 76 | 4.39 | 9.3
| 7 | 125 | 160 | 0.1288 | 108 | 4.31 | 6
| 8 | 125 | 170 | 0.1985 | 126 | 4.4 | 4.8
| 8.5 | 125 | 180 | 0.2149 | 146 | 4.81 | 4.5
| 9 | 125 | 180 | 0.2251 | 168 | 4.46 | 3.6
| 9.5 | 125 | 185 | 0.2492 | 179 | 4.52 | 3.1
| 10 | 125 | 185 | 0.2699 | 190 | 4.25 | 2.8
| 10.5 | 125 | 190 | 0.2934 | 203 | 4.32 | 2.5
| 11 | 125 | 195 | 0.32 | 230 | 4.4 | 2.3
| 11.5 | 125 | 200 | 0.3613 | 251 | 4.48 | 2.1
| 12 | 125 | 200 | 0.3922 | 272 | 4.26 | 1.7
| 13 | 130 | 210 | 0.4366 | 288 | 4.46 | 1.6
MEDIUM | 8.5 | 150 | 215 | 0.2919 | 203 | 8.2 | 9.1
| 9 | 150 | 220 | 0.3149 | 217 | 8.15 | 7.8
| 9.5 | 150 | 225 | 0.3463 | 246 | 8.13 | 6.8
| 10 | 150 | 230 | 0.3599 | 254 | 8.15 | 6.4
| 10.5 | 150 | 235 | 0.3936 | 261 | 8.16 | 5.7
| 11 | 150 | 240 | 0.4298 | 293 | 8.18 | 5
| 11.5 | 150 | 245 | 0.4624 | 319 | 8.21 | 4.5
| 12 | 150 | 250 | 0.4899 | 345 | 8.23 | 4.1
| 13 | 160 | 260 | 0.576 | 376 | 8.46 | 3.7
| 14 | 160 | 275 | 0.6434 | 432 | 8.98 | 3.3
| 15 | 165 | 290 | 0.7651 | 532 | 9.6 | 3.3
| 16 | 170 | 305 | 0.8688 | 591 | 10.23 | 3.1
| 17 | 180 | 320 | 0.9951 | 676 | 11.07 | 3
| 18 | 180 | 330 | 1.1482 | 771 | 11.14 | 2.7
STOUT | 8.5 | 190 | 265 | 0.4171 | 283 | 15.35 | 21.5
| 9 | 190 | 275 | 0.463 | 319 | 15.91 | 19.2
| 9.5 | 190 | 280 | 0.514 | 358 | 15.66 | 16.4
| 10 | 190 | 285 | 0.5502 | 378 | 15.52 | 15.5
| 10.5 | 190 | 290 | 0.5947 | 399 | 15.36 | 13.4
| 11 | 190 | 295 | 0.6533 | 443 | 15.24 | 11.8
| 11.5 | 190 | 300 | 0.6884 | 479 | 15.15 | 10.5
| 12 | 190 | 305 | 0.7428 | 515 | 15.08 | 9.4
| 13 | 195 | 320 | 0.828 | 571 | 15.73 | 8.3
| 14 | 195 | 335 | 0.9486 | 633 | 16.24 | 7.3
| 15 | 195 | 350 | 1.0565 | 734 | 16.68 | 6.8
| 16 | 200 | 365 | 1.1737 | 788 | 17.35 | 6.2
| 17 | 200 | 375 | 1.3167 | 843 | 17.2 | 5.4
| 18 | 200 | 390 | 1.5362 | 1120 | 17.51 | 5
| 20 | 200 | 415 | 1.8516 | 1260 | 17.74 | 4.2
| 22 | 200 | 435 | 2.0388 | 1419 | 17.49 | 3.6
| 24 | 200 | 470 | 2.224 | 1646 | 18.36 | 3.3
NOTES 1 & 2 The strength Properties stated here are based on using Unstayed Poles (Cantilevers)

## Drawing guide - obsolete
Drawing arrangement description | Pole arrangement drawing number (Drawings used to construct pole to on site) | Pole Fabrication drawing number (Drawings used by pole fabricators) | To be confirmed with customer before quoting | Default pole Sinking Depths | Minimum pole top diameter before fabrication
Single Pole | 1091231160 | 1091231160 sht5 |  |  | As per standard minimum size shown in BS1990 table
Single Pole Intermediate | 1091380006 sht1 | 1091380006 sht2 |  | 2.6m | As per standard minimum size shown in BS1990 table
Rutter Pole Intermediate | 1091390016 sht1 | 1091390008 sht2 |  | 3.2m | As per standard minimum size shown in BS1990 table
Rutter St Line Section Pole | 1091390016 sht1 | 1091390008 sht2 |  | 3.2m | As per standard minimum size shown in BS1990 table
132kV Rutter Pole | 1091390017 sht1 | 1091390008 sht2 |  | 3.2m | As per standard minimum size shown in BS1990 table
|  | 1091390003 sht2 |  | 2.4m | 12.0m - 224mm or 242mm | Drawings under review by G Hammel of NPG 02.08.13 (bigger sizes are from more up to date version of drawing that we just received).
*Single Pole Straight Line Section / Section Angle Pole up to 20° | 1091390013 sht1 |  |  |  | 13.0m - 230mm or 247mm
*Single Pole Section Angle Pole 20° - 40° | 1091390014 sht1 |  |  |  | 14.0m - 230mm or 247mm
*Single Pole Section Angle Pole 40° -60° | 1091390015 sht1 |  |  |  | 15.0m - 230mm or 247mm
16.0m - 236mm or 253mm
17.0m - 236mm or 253mm
132kV Section / Angle H Pole |  | 1091380003 sht2 C |  |  | 250mm
H Pole Terminal Pole – No cable termination up to 132kV | 1091390019 sht1 | 1091390019 sht2 |  | 2.4m | 250mm
H Pole Terminal Pole – Cable termination (up to 66kV only) | 1091231173 sht4 | 1091231173 sht10 |  | 2.4m | 230mm
H Pole Section Angle Pole 40° - 60° | 1091390018 sht1 | 1091390018 sht2 |  | 2.4m | 250mm
H Pole St Line Section Pole | 1091390020 sht1
H Pole St Line Section Pole (Out of Balance stays) | 1091390021 sht1
H Pole Intermediate (post Insulators) | 1091390022 sht1
Single Section Pole | 1091231191 sht1 | 1091231186 sht1 |  |  | 210mm Stout 250mm Extra Stout
Single Pole | 1091231190 sht3
H Pole Portal type | 1091231165 sht4 | 1091231187 sht1 rev J |  |  | 230mm
H Portal Support | Y104L0112 | Y003X3103 | H Intermediate |  | 205mm
| Y104L0113 |  | H Section |  | 215mm
| Y104L0114 |  | H Angle |  | 20mm above minimum stated tip diameter in BS1990
| Y104L0115 |  | H Angle |  | 20mm above minimum stated tip diameter in BS1990
| Y104L0116 |  | H Terminal |  | 20mm above minimum stated tip diameter in BS1990
Average taper of poles using BS1990 table - 11mm per metre for Stouts - 9mm per metre for Mediums - 7mm per metre for Lights